## Commands
Commands
General command frames
Command Id | Command Name | M/O | Direction
0x00 | Read Attributes | M | client->server
0x02 | Write Attribute | M | client->server
0x06 | Configure Reporting | O | client->server
0x08 | Read Reporting Configuration | O | client->server
0x0A | Report Attributes | O | server->client
0x0C | Discover Attributes | O | client->server
Basic Cluster (0x0000)
Command Id | Command Name | M/O | Direction
-> no commands are received or generated
Power Configuration Cluster (0x0001)
Command Id | Command Name | M/O | Direction
-> no commands are received or generated
Identify Cluster (0x0003)
Command Id | Command Name | M/O | Direction
0x00 | Identify | M | client->server
0x01 | Identify Query | M | client->server
0x00 | Identify Time Query Response | M | server->client
Time Server Cluster(0x000A)
Command Id | Command Name | M/O | Direction
-> no commands are received or generated
OTA Update Cluster (0x0019)
Command Id | Command Name | M/O | Direction
0x00 | Image Notify | M | server->client
0x01 | Query Next Image Request | M | client->server
0x02 | Query Next Image Response | M | server->client
0x03 | Image Block Request | M | client->server
0x05 | Image Block Response | M | server->client
0x06 | Upgrade End Request | M | client->server
0x07 | Upgrade End Response | M | server->client
Poll control Cluster (0x0020)
Command Id | Command Name | M/O | Direction
0x00 | Check in | M | server->client
0x00 | Check in Response | M | client->server
0x01 | Fast Poll Stop | M | client->server
Thermostat Cluster (0x0201)
Command Id | Command Name | M/O | Direction
0x00 | Setpoint Raise/Lower | M | client->server
Thermostat User Interface Cluster (0x0204)
Command Id | Command Name | M/O | Direction
-> no commands are received or generated
Diagnostics Cluster (0x0B05)
Command Id | Command Name | M/O | Direction
-> no commands are received or generated

## Attributes
Attributes
Profile | (0x0104) Home Automation
DeviceID | (0x0301)Thermostat
Cluster: | (0x0000) Basic
Attribute ID | Name | Data Type | R/W | M/O | Reporting | Default | Descriptions
0x0000 | ZCL Version | uint8 | R | M |  | 0x03
0x0001 | Application Version | uint8 | R | O |  | 0x00
0x0002 | Stack Version | uint8 | R | O
0x0003 | HW Version | uint8 | R | O
0x0004 | Manufacturer Name | string | R | O |  | "Danfoss"
0x0005 | Model Identifier | string | R | O |  | "eTRV0100"
0x0006 | Date Code | string | R | O |  | YYYYMMDD
0x0007 | Power Source | enum8 | R | M |  | 0x03
0x0010 | LocationDescription | string (0-16) | R/W | O |  | Empty string (0)
0x4000 | SW Build ID | string (16) | R | O
Cluster: | (0x0001) Power Configuration
Attribute ID | Name | Data Type | R/W | M/O | Reporting | Default | Descriptions
0x0021 | BatteryPercentageRemaining | uint8 | R | O | Yes
Cluster: | (0x0003) Identify
Attribute ID | Name | Data Type | R/W | M/O | Reporting | Default | Descriptions
0x0000 | Identify Time | uint16 | R/W | M |  | 0x0000
0x4000 | Identification button | Boolean | R |  | Yes | 0x00
Cluster: | (0x000A) Time
Attribute ID | Attribute name | Data Type | R/W | M/O | Reporting | Default | Descriptions
0x0000 | Time | UTC | RW | M |  | 0x586E2730 (Jan 5th 2017, 11:00 AM )
0x0001 | TimeStatus | map8 | RW | M |  | 0x00
0x0002 | TimeZone | int32 | RW | O |  | 0
0x0003 | DstStart | uint32 | RW | O
0x0004 | DstEnd | uint32 | RW | O
0x0005 | DstShift | int32 | RW | O |  | 3600
0x0007 | LocalTime | uint32 | R | O
0x0008 | LastSetTime | UTC | R | O |  | 0x586E2730
Cluster: | (0x0019) OTA
Attribute ID | Name | Data Type | R/W | M/O | Reporting | Default | Descriptions
0x0000 | UpgradeServerID | IEEE address | R | M
0x0001 | FileOffset | uint32 | R | O
0x0002 | CurrentFileVersion | uint32 | R | O
0x0003 | CurrentZigBeeStackVersion | uint16 | R | O
0x0004 | DownloadedFileVersion | uint32 | R | O
0x0005 | DownloadedZigBeeStackVersion | uint16 | R | O
0x0006 | ImageUpgradeStatus | enum8 | R | M
0x0007 | Manufacturer ID | uint16 | R | O |  | 0x1246
0x0008 | Image Type ID | uint16 | R | O
0x0009 | MinimumBlockPeriod | uint16 | R | O
0x000A | Image Stamp | uint16 | R | O
Cluster: | (0x0020) Poll Control
Attribute ID | Name | Data Type | R/W | M/O | Reporting | Default | Descriptions
0x0000 | Check-in Interval | uint32 | R/W | M |  | 1200
0x0001 | Long Poll Interval | uint32 | R | M |  | 28
0x0002 | Short Poll Interval | uint16 | R | M |  | 2
0x0003 | Fast Poll Timeout | uint16 | R/W | M |  | 40
0x0004 | Check-in Interval Min | uint32 | R | O |  | 240
0x0005 | Long Poll Interval Min | uint32 | R | O |  | 28
0x0006 | Fast Poll Timeout Max | uint16 | R | O |  | 60
Cluster: | (0x0201) Thermostat
Attribute ID | Name | Data Type | R/W | M/O | Reporting | Default | Descriptions
0x0000 | Local Temperature | Int16 | R | M | Yes
0x0003 | absMinHeatSetpointLimit | Int16 | R | O |  |  | Manufacturer specific: absolute minimum temperature in centigrades
0x0004 | absMaxHeatSetpointLimit | Int16 | R | O |  |  | Manufacturer specific: absolute maximum temperature centigrades
0x0008 | PIHeatingDemand | uint8 | R | O | Yes | - | Level of heating demanded by the PI loop in percent 0: when the thermostat is in “off”
0x0010 | LocalTemperatureCalibration | Int8 | R/W | O |  | 0x00 | in steps of 0.1°C. The range of this offset is –2.5 °C to +2.5 °C).
0x0012 | OccupiedHeating Setpoint | Int16 | R/W | M | Yes | 0x834
0x0015 | MinHeatSetpointLimit | Int16 | R/W | O |  | absMinHeat SetpointLimit
0x0016 | MaxHeatSetpointLimit | Int16 | R/W | O |  | absMaxHeat SetpointLimit
0x001B | Control Sequence of Operation | enum8 | R/W | M |  | 0x02 | Heating Only (0x02).
0x001C | System Mode | enum8 | R/W | M |  | 0x04 | 0x04: Heating control active Everything else rejected with INVALID_VALUE
0x4000 | eTRV Open Window Detection | enum8 | R |  | Yes | 0x00 | 0x00: Quarantine 0x01: Windows are closed 0x02: Hold ,Windows are maybe about to open 0x03: Open window detected 0x04: In window open state from external, but detected closed locally
0x4003 | External Open Window Detected | boolean | R/W |  |  | 0x00 | 0x00: Windows are closed 0x01: Windows are opened
0x4010 | Exercise day of week | enum8 | R/W |  |  | 0x04 | 0 = Sunday, 1 = Monday, … 6 = Saturday, 7 = undefined
0x4011 | Exercise trigger time | uint16 | R/W |  |  | 660 | Minutes since midnight, 0xFFFF = undefined
0x4012 | Mounting mode active | boolean | R |  | Yes | 0x01 | 0x01: Not mounted (after factory reset) 0x00: Mounted
0x4013 | Mounting mode control | boolean | R/W |  |  |  | 0x00 Go to mounting mode (the eTRV can now be mounted on a valve) 0x01 Go to Mounted posittion (the eTRV now act as if it's mounted on a valve)
0x4014 | eTRV Orientation | boolean | R/W |  |  | 0x00 | 0x00: Horizontal (Default) 0x01: Vertical
0x4015 | External Measured Room Sensor | Int16 | R
0x4020 | Control algorithm scale factor | uint8 | R/W |  |  | 1 | Scale factor of setpoint filter timeconstant ("aggressiveness" of control algorithm) 1= Quick ... 5=Moderate ... 10=Slow
0x4030 | Heat Available | boolean | R/W |  |  | 0x01 | 0x00 No heat available 0x01 Heat avaliable
0x4031 | Heat Supply Request | boolean | R |  |  |  | 0x00 No heat request 0x01 Heat request
Cluster: | (0x0204) Thermostat UI Configuration
Attribute ID | Name | Data Type | R/W | M/O | Reporting | Default | Descriptions
0x0000 | TemperatureDisplayMode | enum8 | R/W | M |  | 0x00 | 0x00 = °C 0x01 = °F Not supported!
0x0001 | KeypadLockout | enum8 | R/W | M |  | 0x00 | 0x00 = no lockout 0x01 = level 1 lockout
0x4000 | Viewing Direction | enum8 | R/W |  |  | 0x00 | 0x00 = viewing direction 1 0x01 = viewing direction 2
Cluster: | (0x0B05) Diagnostic
Attribute ID | Name | Data Type | R/W | M/O | Reporting | Default | Descriptions
0x011C | LastMessageLQI | uint8 | R | O |  | 0x00 | The Link Quality Indicator is a value between 0 and 255 where 0 indicates the worst possible link and 255 indicates the best possible link.
0x011D | LastMessageRSSI | int8 | R | O |  | 0 | This is the receive signal strength indication (in dBm) for the last message received.
0x4000 | SW error code | map16 | R/W |  | Yes | 0